| Issued to: |  | BERMAD INC |
| --- | --- | --- |
|  |  | 1849 Thunderbolt Drive Porterville CA 93257 |
| This is to certify that representative samples of |  | Special System Water Control Valves, Pressure-reducing and Pressure-control Type Special System Water Control Valves, Class II |
|  |  | See Addendum Page |
|  |  | Have been investigated by UL in accordance with the Standard(s) indicated on this Certificate. |
| Standard(s) for Safety: |  | UL 1739 - Pilot-Operated Pressure-Control Valves for Fire-Protection Service |
| Additional Information: |  | See the UL Online Certifications Directory at www.ul.com/database for additional information |

Only those products bearing the UL Certification Mark should be considered as being covered by UL's Certification and Follow-Up Service.

Look for the UL Certification Mark on the product.

This is to certify that representative samples of the product as specified on this certificate were tested according to the current UL requirements.

The pilot operated pressure control valves are intended to reduce the water pressure in the supply piping for standpipe systems and/or sprinkler systems in the following models, types, sizes and pressures:

| Certification | Model | Body Type | Nominal Pipe Size, NPS | End Configuration* | Max. Rated Inlet Pressure, psig | Outlet Pressure Setting Range, psig |
| --- | --- | --- | --- | --- | --- | --- |
| USL, CNL | 720 | Globe, Angle | 2, 2-1/2 | T by T | 300 | 30-165 |
| * |  |  |  |  |  |  |
| USL, CNL | 720 | Globe, Angle | 2, 2-1/2, 3,4,6 | Class 150-F by F, G by G | 250 | 30-165 |
| *USL, CNL | 720 | Globe, Angle | 2, 2-1/2, 3,4,6 | Class 300-F by F, G by G | 300 | 30-165 |
| USL, CNL | 720 | Globe, Angle | 8 | Class 150-F by F, G by G | 175 | 40-165 |

F- Flange

*T- NPT or ISO thread

*- End configurations are intended to be installed on systems not exceeding end configurations working capabilities.